## VFD Savings
Generic VFD Savings Calculation Spreadsheet
The user should input project specific data into the yellow shaded cells.
Cells in Row 23 describe the motor(s) being controlled in terms of HP, % loading at 100% output level for the process, and motor nominal efficiency.
Cell E29 is the power-to-speed reduction exponent. For closed systems where friction represents a high % of overall head, the exponent will be close to 3.0
and the input power with vfd will follow affinity laws (input power varies as the cube of % speed). For closed systems where total head is not predominantly
from friction losses, the exponent should be between 2.0 and 3.0. For open systems, or systems where friction head is negligible compared to overall head,
like a high pressure boiler feed water pump, the exponent will be close to 1.0. Please enter you best estimate of the exponent that is most appropriate for
your application.
Cell E30 and E31 should be populated with VFD manufacturers data.
Cell F33 represent the method of control that most closer describes the baseline situation.
Cells H35 and I35 represent the annual hours of operation for the baseline and the proposed case.
The range from cell B41:D53 should be used to describe the load shape of the operation. Inputs to this range should be supported by historical data, or
clearly explained.
Description | HP | Quantity | Estimated Load | Efficiency | Demand kW | Total Demand kW
Chilled water pump | 25 | 1 | 70% | 88.5% | 14.7514 | 14.7514
Existing Process Pumps Demand |  |  | 14.7514 | kW
VFD Parameters
Power-to-Speed Reduction Exponent |  |  | 2.5 | Range = 1.0 - 3.0
Safe Minimum Motor Speed |  |  | 30%
Average VFD Efficiency Penalty at Full Speed |  |  | 2%
IDENTIFY EXISTING METHOD OF CONTROL
1=No Control, 2=Fan/Blower Inlet Guide Vanes, 3=Pump Throttling or Fan/Blower Outlet Discharge Dampers
[6 empty] | Existing | Proposed
[5 empty] | Annual Hours of Operation: | 5000 | 5000
Output | Percent | Estimated | Existing | Proposed | Existing | Proposed | Energy
Load | of full | %Time at | w/o VFD | w/VFD | w/o VFD | w/VFD | Savings
Level | load speed | Load | kW | kW | kWh | kWh | kWh
100% | 100% | 15% | FALSE | 15.0525 | 0 | 11289.3462 | -11289.3462
95% | 95% | 15% | FALSE | 13.2409 | 0 | 9930.653 | -9930.653
90% | 90% | 15% | FALSE | 11.5668 | 0 | 8675.1115 | -8675.1115
85% | 85% | 15% | FALSE | 10.0266 | 0 | 7519.97 | -7519.97
80% | 80% | 15% | FALSE | 8.6165 | 0 | 6462.3989 | -6462.3989
75% | 75% | 15% | FALSE | 7.3326 | 0 | 5499.4841 | -5499.4841
70% | 70% | 10% | FALSE | 6.171 | 0 | 3085.4793 | -3085.4793
65% | 65% | 10% | FALSE | 5.1273 | 0 | 2563.6629 | -2563.6629
60% | 60% | 10% | FALSE | 4.1975 | 0 | 2098.7256 | -2098.7256
55% | 55% | 0% | FALSE | 3.3769 | 0 | 0 | 0
50% | 50% | 0% | FALSE | 2.6609 | 0 | 0 | 0
45% | 45% | 0% | FALSE | 2.0447 | 0 | 0 | 0
40% | 40% | 0% | FALSE | 1.5232 | 0 | 0 | 0
|  | 120% |  | TOTALS | 0 | 57124.8316 | -57124.8316
Fan Power Requirements
Percent Full | Percent of Full Speed Input Power with
Speed or Flow |  | Discharge | Inlet Guide
Flow | No control | Dampers | Vane | VFD
100% | 100% | 100% | 100% | 100%
80% | 100% | 95% | 78% | 51.2%
60% | 100% | 87% | 61% | 21.6%
40% | 100% | 75% | 51% | 6.4%
20% | 100% | 60% | 43% | 0.8%
0% | 100% | 41% | 39% | 0%
Notes | 1 | 2 | 3 | 4
Curve Fit Polynomial Equations
% Power = a x % speed^2 = b x % speed + c
Coefficients |  |  |  |  | a | b | c
fan/blower inlet guide vanes |  |  |  |  | 0.5625 | 0.0375 | 0.395
pump throttling or fan/blower discharge damper |  |  |  |  | -0.4196 | 1.0096 | 0.4107
Notes 1 - 100 percent of full speed power 4 - Affinity law only. (Note: separate consideration given to minimum static pressure requirement and VFD efficiency.)